SECTION 27 51 29

EMERGENCY COMMUNICATIONS SYSTEMS

PART 1 GENERAL

1.01   SUMMARY

- Equipment and materials used shall be standard components that are manufactured and available for purchase as standard replacement parts as long as the product is commercially available from the manufacturer.

1.02   QUALITY ASSURANCE

- All station installation, configurations, setup, programming, and related work shall be performed by electronic technicians thoroughly trained by the manufacturer in the installation and service of the equipment provided.

- All equipment shall be warrantied against any defects in material and workmanship under normal use for a period of sixty (60) months from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the sixty (60) months will commence on the date of shipment by the manufacturer.

1.03   CERTIFICATIONS AND STANDARDS

- The station shall be designed to meet the following standards:

  - Accessibility

    - ADA: Standards for Accessible Design – 2010 §7

    - ANSI ICC A117.1 (2009): Accessible and Usable Buildings and Facilities

    - IBC (2018) §1009

    - Illinois Accessibility Code

    - NFPA 72: National Fire Alarm and Signaling Code – 2016 §24.10

  - Safety

    - UL 60950-1

  - Networking:

    - IEEE 802.3af (Power over Ethernet)

    - TCP/IP (RFC 1122)

    - IPv4 (RFC 791)

PART 2 PRODUCTS

2.01   GENERAL

- The station shall:

  - Consist of an indoor-rated vandal resistant ADA-compliant hands-free area of refuge two-way communication device with a stainless steel faceplate and metal button.

  - Have, at minimum, an IP31 ingress protection rating.

  - Be surface or wall mountable.

  - Be full duplex in operation.

  - Be programmable from a remote location.

  - Be configured to dial from a list of telephone numbers in round robin fashion until the call is answered.

2.02   HARDWARE

- The station faceplate shall:

  - Be constructed of a 304 grade stainless steel plate with provisions for a primary button, primary signage, a hands-free speaker, a hands-free microphone, and an LED indicator.

  - Have a thickness of 0.09” (2.2mm).

  - Measure 4.75” W x 8.23” H.

- The station faceplate primary signage shall:

  - Be constructed of 304 grade stainless steel with lettering and braille raised for ADA compliance.

  - Lettering shall be raised no less than 0.03125”.

  - Braille shall be raised no less than 0.025”.

  - Read “EMERGENCY”.

  - Be printed red.

- The primary button shall:

  - Be a high quality 0.88” diameter push button (1.10” overall diameter) and switch in a single assembly.

  - The switch shall be mechanically rated to 50,000 cycles (typical).

  - Provide tactile feedback.

  - Have an operating temperature range of -40°F (-40°C) to +185°F (+85°C).

  - Have an enclosure design that is watertight as per IP67 rating.

  - Be constructed of an aluminum alloy, with a clear chromate finish.

  - Have a metal cap, painted red with a UV-resistant finish.

- The station shall have one (1) 3mm diameter red light emitting diode (LED).

- The speaker shall:

- Be a 2.5” round, RoHS compliant, outdoor rated speaker.

- Have an operating temperature range of -67°F (-55°C) to +185°F (+85°C).

- Be capable of withstanding a total immersion for 96 hours and operating without any deterioration of sound quality.

- Have a speaker cone constructed of a corrosion resistant material.

- Be constructed of a neodymium magnet and a solid aluminum voice coil and shall be adequately protected from ferrous and non-ferrous particles via a sealed design.

- The microphone shall:

- Be a 6mm diameter, aluminum construction, RoHS compliant, outdoor rated microphone.

- Have an IP57 type enclosure to protect from dust and water.

- Have an operating temperature range of -40°F (-40°C) to +158°F (+70°C).

- Operate within ±3db of initial sensitivity after being placed in a chamber at +40°C and 90±5% relative humidity for 240 hours (tested after 6 hours of conditioning at +25°C).

- The station shall weigh approximately 4 lbs.

- The back box enclosure shall:

  - Measure 5.5” W x 8.38” H x 2.0” D.

  - Be constructed of Cold Rolled Steel (CRS).

2.03   AUDIO

- The station shall support full duplex audio.

- The station shall support acoustic echo cancellation.

2.04   FUNCTIONALITY

- Web Server

  - The station shall contain a built-in web server making configuration available to multiple clients in a standard operating system and browser environment using HTTP or HTTPS, without the need for additional software.

  - The web server shall require authentication with username and password.

- IP Address

  - The station shall support both fixed IP addresses and dynamically assigned IP addresses provided by a Dynamic Host Control Protocol (DHCP) server.

  - The station shall support IPv4.

- Telephone Calls

  - The station shall be programmable to dial from a list of telephone numbers in round robin fashion until the call is answered.

  - When the call is finished, the station shall automatically terminate the call.

  - The station shall be capable of auto-answering any call placed to it from a local command unit phone.

- Hearing Impairment Aid (LED)

- The station shall have one (1) LED to indicate the status of a call.

- Voice Messages

- The station shall be capable of automatically playing a prerecorded voice message to the attendant at the local command unit phone.

- This prerecorded voice message shall notify the attendant of the station location by playing at the beginning of the phone conversation.

- An attendant through a PSTN connection will not receive a prerecorded voice message from the station.

- Protocol Support

- The station shall incorporate support for at least IPv4, HTTPS, TCP, UDP, RTP, RTCP, and DHCP.

- Installation and Maintenance

- All configurable settings, including statically assigned IP address and audio configuration, shall be stored in non-volatile memory and shall not be lost during power cuts or soft reset.

2.05   INTERFACES

- Network Interfaces

  - The station shall be equipped one (1) 10/100 Base-T Ethernet port.

2.07   POWER REQUIREMENTS

  - The station shall be powered via Power over Ethernet (IEEE 802.3af) through an Ethernet switch.

  - The Ethernet switch shall be powered through an Uninterruptible Power Supply (UPS) which provides either four (4) or twenty-four (24) hours of battery backup depending on local jurisdiction requirements.

2.08   ENVIRONMENTAL

- The station shall:

  - Operate in a temperature range of -40°F (-40°C) to + 158°F (+70°C).

  - Operate in a humidity range up to 95% RH (non-condensing).

2.09   MANUFACTURED UNITS

- The station shall be a Talkaphone AOR-IP-CSE-SM Area of Refuge Station.

PART 3 EXECUTION

3.01      INSTALLATION

- The installer shall carefully follow instructions in documentation provided by the manufacturer to ensure all steps have been taken to provide a reliable, easy-to-operate system.

- All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

- All firmware found in products shall be the latest and most up-to-date provided by the manufacturer.

- All equipment requiring users to log on using a password shall be configured with user/site-specific password/passwords.  No system/product default passwords shall be allowed.

END OF SECTION