SECTION 10 17 16

TELEPHONE ENCLOSURES

PART 1 GENERAL

1.01   SUMMARY

- Equipment and materials used shall be standard components that are manufactured and available for purchase as standard replacement parts as long as the product is commercially available from the manufacturer.

1.02   QUALITY ASSURANCE

- All pedestal mount installation, configurations, setup, program and related work shall be performed by electronic technicians thoroughly trained by the manufacturer in the installation and service of the equipment provided.

- The pedestal mount shall be warrantied against any defects in material and workmanship under normal use for a period of five (5) years from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the five (5) years will commence on the date of shipment by the manufacturer.

- The faceplate light shall be warrantied against any defects in material and workmanship under normal use for a period of twenty-four (24) months from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the twenty four (24) months will commence on the date of shipment by the manufacturer.

1.03   CERTIFICATIONS AND STANDARDS

- The pedestal mount as an assembly shall be certified to:

  - UL Std 60950-1

PART 2 PRODUCTS

2.01   GENERAL

- The pedestal mount shall:

  - Consist of a highly vandal-resistant free-standing steel emergency phone pedestal mount.

  - Have an integrated LED faceplate light, mounted directly above the phone faceplate.

2.02   HARDWARE

- The pedestal mount shall:

  - Be constructed of 0.25” thick steel and weigh approximately 120 lbs.

  - Measure 12” W x 8” D x 48” H, with a 2” radius on each corner.

  - Utilize a high-gloss, multi-coat, corrosion-inhibitive coating that shall be applied to withstand prolonged exposure to hard environments.

    - Pedestal mount shall be sandblasted to SSPC-6 standards before a 2-3 mil layer of rust-inhibitive primer is applied.

    - Pedestal mount shall be hand sanded for smoothness before a second 2-3 mil layer of primer is applied.

    - Pedestal mount shall have a 2-3 mil layer of customer specified color coat applied.

    - Pedestal mount shall have a 1-2 mil layer of clear coat applied.

- The pedestal mount base plate shall:

  - Be 2.0” above the pedestal base.

  - Be constructed of 0.50” A-36 Structural Steel.

  - Have a 4” diameter center hole for wiring access.

  - Have four 1” holes for anchor bolt attachment.

- The pedestal mount wiring access opening shall:

  - Measure 9.75”H x 6” W.

  - Be located 11” above the base of the pedestal mount.

  - Have a flush cover plate that shall:

    - Be constructed of 0.25” thick steel.

    - Be held in place by two 1/4" countersunk, tamper-resistant spanner screws.

- The pedestal mount shall have an opening in the front to accommodate flush mounting an emergency phone. The phone opening shall:

  - Measure 10” H x 6.75” W.

  - Have six self-clinching 10-24 stainless steel threaded nuts to mount the emergency phone.

- The pedestal mount shall have the word “EMERGENCY” emblazoned on all four sides in 3.25” high reflective white letters. Custom lettering, sizes and colors are available.

2.03   FUNCTIONALITY

- Faceplate Light

  - The faceplate light shall remain lit at all times.

  - The faceplate light shall have a concealed, ultra-bright LED design.

  - The faceplate light LEDs shall have no less than 50,000 hour lifetime.

2.04   POWER REQUIREMENTS

- The pedestal mount shall be powered by one of the following power sources:

  - 12VDC – Nominal: 1.2 Watts

  - 24VDC – Nominal: 1.2 Watts

  - 24VAC – Nominal: 1.2 Watts

  - 120VAC – Nominal: 1.2 Watts

2.05   MANUFACTURED UNITS

- The pedestal mount shall be a Talkaphone ETP-PM Emergency Telephone Pedestal Mount.

PART 3 EXECUTION

3.01      INSTALLATION

- The Contractor shall carefully follow instructions in documentation provided by the manufacturer to ensure all steps have been taken to provide a reliable, easy-to-operate system.

- All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

- The pedestal mount shall include 24-inch long J-bolts for mounting into a 24” x 24” concrete foundation. Depth to vary according to local regulations and other site-specific considerations.

- The J-bolts shall protrude approximately 5 inches from the surface of the foundation.

END OF SECTION