SECTION 10 17 16

TELEPHONE ENCLOSURES

PART 1 GENERAL

1.01   SUMMARY

- Equipment and materials used shall be standard components that are manufactured and available for purchase as standard replacement parts as long as the product is commercially available from the manufacturer.

1.02   QUALITY ASSURANCE

- All wall mount installation, configurations, setup, program, and related work shall be performed by electronic technicians thoroughly trained by the manufacturer in the installation and service of the equipment provided.

- The wall mount shall be warrantied against any defects in material and workmanship under normal use for a period of five (5) years from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the five (5) years will commence on the date of shipment by the manufacturer.

- The blue light shall be warrantied against any defects in material and workmanship under normal use for a period of twenty-four (24) months from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the twenty-four (24) months will commence on the date of shipment by the manufacturer.

1.03   CERTIFICATIONS AND STANDARDS

- The wall mount shall be designed to meet the following standards:

  - UL Std 60950-1

  - UL Std 60950-22

- The included LED blue light (model: ETP-EL or ETP-EL12/24) shall be certified to:

  - UL Std 1598

  - CSA Std C22.2 No. 250.0

PART 2 PRODUCTS

2.01   GENERAL

- The wall mount shall:

  - Consist of a vandal-resistant, pole or wall mountable, SAE 316 stainless steel emergency phone mount with an integrated flashing LED blue light.

2.02   HARDWARE

- The wall mount shall:

  - Be constructed of SAE 316 marine grade stainless steel and weigh approximately 23 lbs.

  - Measure 10” W x 4” D x 32” H.

  - Have four 0.27” diameter mounting holes on the rear of the enclosure.

  - Have three 1-1/8” knockouts on the rear of the enclosure for 3/4” conduit.

  - Have two 1-1/8” knockouts on the underside of the enclosure for 3/4” conduit.

- The wall mount shall have an opening in the front to accommodate flush mounting an emergency phone.  The phone opening shall:

  - Measure 10.25” H x 7.00” W.

  - Have six self-clinching #10-24 stainless steel threaded nuts to mount the emergency phone.

- The wall mount shall have the word “EMERGENCY” emblazoned on all four sides in 2.00” high reflective red letters.  Custom lettering, sizes, and colors are available.

- The wall mount blue light shall:

  - Be mounted within an enclosed protective polycarbonate housing.

  - Have a polycarbonate refractor lens assembly with a prismatic pattern to increase visibility at greater distances.

2.03   FUNCTIONALITY

- Blue Light

  - The blue light shall remain lit at all times.

  - The blue light shall automatically flash 78 times per minute when triggered by the emergency phone.

  - The blue light shall retain 70% of its initial output intensity after 50,000 hours of operation.

2.04   POWER REQUIREMENTS

- The wall mount shall be powered by one of the following power sources:

  - 12VDC – Nominal: 7.5 Watts

  - 24VDC – Nominal: 7.5 Watts

  - 24VAC – Nominal: 7.5 Watts

  - 120VAC – Nominal: 7.8 Watts

2.05   MANUFACTURED UNITS

- The mount shall be a Talkaphone ETP-WMSE Emergency Telephone Wall Mount.

PART 3 EXECUTION

3.01      INSTALLATION

- The Contractor shall carefully follow instructions in documentation provided by the manufacturer to ensure all steps have been taken to provide a reliable, easy-to-operate system.

- All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

END OF SECTION