SECTION 27 51 29

EMERGENCY COMMUNICATIONS SYSTEMS

PART 1 GENERAL

1.01   SUMMARY

- Equipment and materials used shall be standard components that are manufactured and available for purchase as standard replacement parts as long as the product is commercially available from the manufacturer.

1.02   QUALITY ASSURANCE

- All UPS supervisor installation, configurations, setup, programming, and related work shall be performed by electronic technicians thoroughly trained by the manufacturer in the installation and service of the equipment provided.

- All equipment shall be warrantied against any defects in material and workmanship under normal use for a period of sixty (60) months from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the sixty (60) months will commence on the date of shipment by the manufacturer.

1.03   CERTIFICATIONS AND STANDARDS

- The UPS supervisor shall be designed to meet the following standards:

  - UL 864

PART 2 PRODUCTS

2.01   GENERAL

- The UPS supervisor shall:

  - Be a monitoring device that supervises an area of refuge uninterruptible power supply (UPS).

  - Provide a relay contact output should it detect that primary or utility power to the UPS is not available.

  - Be surface mountable.

2.02   HARDWARE

- The UPS supervisor shall:

  - Have an enclosure with a removable cover constructed of acrylonitrile butadiene styrene (ABS) with a rating of 94 V-0.

  - Have an enclosure that can be surface mounted.

  - Measure 3.15” W x 2.63” D x 5.31” H.

- The UPS supervisor shall weigh approximately 0.85 lbs.

2.03   FUNCTIONALITY

- The UPS supervisor shall have one (1) red light emitting diode (LED) which illuminates when the relay coil is energized.

2.04   INTERFACES

- Relay Contact Output

  - The UPS supervisor shall be equipped with one (1) relay contact output, accessible from a built-in terminal block.

    - The relay contact output shall have a rating of 7A at 28VDC, 10A (NO:1/6HP, NC:1/8HP) at 120VAC, and 7A at 230VAC.

    - The relay contact output shall be a double pole, double throw (DPDT) type with dry Form C contacts.

2.05   POWER REQUIREMENTS

  - The UPS supervisor shall be powered through an Uninterruptible Power Supply (UPS) which provides either four (4) or twenty-four (24) hours of battery backup depending on local jurisdiction requirements.

  - The UPS shall provide 120VAC, 50/60Hz, 45mA to the UPS supervisor.

2.06   ENVIRONMENTAL

- The UPS supervisor shall:

  - Operate in a temperature range of 32°F (0°C) to + 120°F (+49°C).

  - Operate in a humidity range of up to 93% RH (non-condensing, non-freezing) at 89.6°F.

2.07   MANUFACTURED UNITS

- The UPS supervisor shall be a Talkaphone AOR-IP-UPS-SUP UPS supervisor.

PART 3 EXECUTION

3.01      INSTALLATION

- The installer shall carefully follow instructions in documentation provided by the manufacturer to ensure all steps have been taken to provide a reliable, easy-to-operate system.

- All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

END OF SECTION