SECTION 27 32 26

RING-DOWN EMERGENCY TELEPHONES

PART 1 GENERAL

1.01   SUMMARY

- Equipment and materials used shall be standard components that are manufactured and available for purchase as standard replacement parts as long as the product is commercially available from the manufacturer.

1.02   QUALITY ASSURANCE

- All phone installation, configurations, setup, program and related work shall be performed by electronic technicians thoroughly trained by the manufacturer in the installation and service of the equipment provided

- All equipment shall be warrantied against any defects in material and workmanship under normal use for a period of twenty-four (24) months from date of installation, provided that manufacturer receives a completed "Installation Certification" certifying the date on which the system has been installed.  An "Installation Certification" card shall be enclosed with every unit.  In the event that no "Installation Certification" is received by manufacturer, the twenty four (24) months will commence on the date of shipment by the manufacturer.

1.03   CERTIFICATIONS AND STANDARDS

- The phone shall carry the following EMC approvals:

  - FCC (47 CFR 15, Subpart B)

- The phone shall meet the following standards:

  - Accessibility

    - ADA: Standards for Accessible Design – 2010

    - ANSI ICC A117.1 (2009): Accessible and Usable Buildings and Facilities

    - NFPA 72: National Fire Alarm and Signaling Code – 2013

    - NFPA 101: Life Safety Code® 2012

    - Illinois Accessibility Code

  - Networking:

    - IEEE 802.3af (Power over Ethernet)

    - TCP/IP (RFC 1122)

    - IPv4 (RFC 791)

    - SIP (RFC 3261)

    - QoS – Diffserv (RFC 2475)

PART 2 PRODUCTS

2.01   GENERAL

- The phone shall:

  - Consist of an outdoor-rated vandal resistant ADA-compliant hands-free speakerphone communications device with a bonded PET and marine-grade stainless steel faceplate with metal button(s).

  - Be full duplex in operation.

  - Be programmable from a remote location.

  - Have a six number dialing capability, reverting to the subsequent number if the first is busy or does not respond.

2.02   HARDWARE

- The phone faceplate shall:

  - Be constructed of a 304 grade stainless steel base plate bonded with a:

    - Enhanced corrosion resistant #4 brushed 316 grade stainless steel signage plate.

    - UV-resistant Polyethylene Terephthalate (PET) dead-front signage panel.

  - Have a combined thickness of 0.086” (2.13mm)

  - Measure 8.5” W x 11.5” H.

- The phone faceplate primary signage shall:

  - Be constructed of enhanced corrosion resistant 316 grade stainless steel with lettering and Braille raised for ADA compliance.

  - Lettering shall be raised no less than 0.03125”.

  - Braille shall be raised no less than 0.025”.

  - Read “EMERGENCY”.

  - Be printed red and have a UV-resistant finish.

- The phone faceplate secondary signage shall:

  - Be constructed of enhanced corrosion resistant 316 grade stainless steel with lettering and Braille raised for ADA compliance.

  - Lettering shall be raised no less than 0.03125”.

  - Braille shall be raised no less than 0.025”.

  - Read “INFO”.

  - Be printed black and have a UV-resistant finish.

- The primary button shall:

  - Be a high quality 1.375” diameter push button (1.80” overall diameter) and switch in a single assembly.

  - The switch shall be mechanically rated to 50,000 cycles (typical).

  - Provide tactile feedback.

  - Have an operating temperature range of -40°F (-40°C) to +185°F (+85°C).

  - Have an enclosure design that is watertight as per IP67 rating.

  - Be constructed of an aluminum alloy, with a clear chromate finish.

  - Have a metal cap, painted red with a UV-resistant finish.

- The secondary button shall:

- Be a high quality 0.78” diameter push button (1.10” overall diameter) and switch in a single assembly.

- The switch shall be mechanically rated to 50,000 cycles (typical).

- Provide tactile feedback.

- Have an operating temperature range of -40°F (-40°C) to +185°F (+85°C).

- Have an enclosure design that is watertight as per IP67 rating.

- Be constructed of an aluminum alloy, with a clear chromate finish.

- Have a metal cap, painted black with a UV-resistant finish.

- The phone shall have three light emitting diode (LED) lit dead-front messages, labeled "CALLING", "ANSWERED", and "HELP ON THE WAY".

- The speaker shall:

- Be a 3.5” round, RoHS compliant, outdoor rated speaker.

- Have an operating temperature range of -67°F (-55°C) to +185°F (+85°C).

- Be capable of withstanding a total immersion for 96 hours and operating without any deterioration of sound quality.

- Have a speaker cone constructed of a corrosion resistant material.

- Be constructed of a neodymium magnet and a solid aluminum voice coil and shall be adequately protected from ferrous and non-ferrous particles via a sealed design.

- The microphone shall:

- Be a 6 mm diameter, aluminum construction, RoHS compliant, outdoor rated microphone.

- Have an IP57 type enclosure to protect from dust and water.

- Have an operating temperature range of -40°F (-40°C) to + 158°F (+70°C).

- Operate within ±3db of initial sensitivity after being placed in a chamber at +40°C and 90±5% relative humidity for 240 hours. (Tested after 6 hours of conditioning at +25°C)

- The phone shall weigh approximately 5 lbs.

- The phone shall have an ABS back box mounted on four 6-32 studs to protect electronics from unintentional installer interaction.

2.03   AUDIO

- The phone shall support full duplex audio using G.711 PCM a-Law, G.711 PCM u-Law, G.729a, and G.723.1a compression.

- The phone shall be capable of providing 8-bit audio at up to 64Kbit/sec.

- The phone shall be capable of providing sound greater than 90dBC at one meter for normal conversation.

- The phone shall be capable of providing sound greater than 100dBC at one meter for paging mode.

- The phone shall support Voice Activity Detection and Comfort Noise Generation.

- The phone shall support Acoustic Echo Cancellation.

- The phone shall support Auto Gain Control.

- The phone shall have configurable Jitter Buffer.

2.04   FUNCTIONALITY

- Web Server

  - The phone shall contain a built-in web server making configuration available to multiple clients in a standard operating system and browser environment using HTTP, without the need for additional software.

  - The web server shall require authentication with username and password.

- IP Address

  - The phone shall support both fixed IP addresses and dynamically assigned IP addresses provided by a Dynamic Host Control Protocol (DHCP) server.

  - The phone shall support IPv4.

- Bandwidth Management

  - The phone shall support Differentiated Services (DiffServ) to provide Quality of Service (QoS) and to prioritize traffic.

- Voice over Internet Protocol (VoIP)

  - The phone shall be configurable with up to three SIP registrars. Each registrar can be configured for:

    - Broadcast Domain

    - SIP Username

    - SIP Password

    - SIP Registrar IP Address

    - SIP Registrar Port

    - SIP Re-registration Time

  - The phone shall be configurable with up to three outbound proxies. Each outbound proxy can be configured for:

    - Outbound Proxy Username

    - Outbound Proxy Password

    - Outbound Proxy IP Address

- Telephone Calls

  - The phone shall be programmable with up to six different telephone numbers of up to 30 digits for each of six telephone number lists.

    - If the first number does not answer or is busy, the phone shall automatically call the second number.

    - If the second number does not answer or is busy, the phone shall automatically call the third number.

    - The phone shall continue dialing in round robin fashion until the call is answered or the call conversation timer limit expires.

  - The phone shall have a call conversation timer that is user configurable from 1 to 360 minutes.

  - The phone shall have a ringback or busy timer that is user configurable from 1 to 60 seconds.

  - The phone shall have a hang-up on silence timer that is user configurable from 10 to 360 seconds.

  - When the call is finished, the phone shall automatically terminate the call.

  - The phone shall be capable of auto answering any call placed to it from another telephone.

  - The phone shall be capable of silently answering an incoming call for monitoring.

- Hearing Impairment Aides (LEDs)

- The phone shall illuminate an LED message, labeled “CALLING”, when calling party has placed a call.

- The phone shall illuminate an LED message, labeled “ANSWERED”, when the call has been answered by the remote attendant.

- The phone shall illuminate an LED message, labeled “HELP ON THE WAY”, when the remote attendant enters a predefined DTMF command.

- Voice Messages

- The phone shall be programmable with up to five unique voice messages.

- The phone shall be capable of automatically notifying the remote attendant of the emergency phone location via a recorded message that plays at the beginning of the phone conversation.

- The voice messages shall be configured as responses to event triggers.

- Event Functionality

- The phone shall be equipped with integrated event functionality which can be triggered by:

    - Primary button activation

    - DTMF tone

    - Auxiliary Input activation

    - Auxiliary Input deactivation

    - Call termination

- The responses to triggers shall include:

- Placing a telephone call

- Activating one or multiple auxiliary outputs

- Notification using TCP (ASCII format)

- Activation of a voice message

- Enabling paging mode

- Disabling paging mode

- Sending an email via SMTP

- Event functions shall be configurable from the web interface.

- Email Notification Profiles

- The phone shall be configurable with up to four email recipients for each of three email notification profiles.

- The phone shall be configurable to send an email when triggered by:

- Emergency Call

- Information Call

- System Restore – Ethernet up

- System Restore – Firmware Upgrade Fail

- SIP Registration

- SIP Deregistration

- Aux Output 1 Activation

- Aux Output 2 Activation

- Aux Output 3 Activation

- Aux Input 1 Activation

- Aux Input 1 Deactivation

- Aux Input 2 Activation

- Aux Input 2 Deactivation

- Aux Input 3 Activation

- Aux Input 3 Deactivation

- Paging Mode

- The phone shall support a user configurable paging mode, where the microphone is disabled and the audio is passed either to the speaker or to the line-level output.

- The phone shall be configurable to enable paging mode automatically on incoming calls.

- The phone shall be configurable to enable/disable paging mode based on DTMF events.

- The phone shall support user configurable output gain for paging mode.

- Diagnostics

- The phone shall support logging of phone events, call statistics, call details, and auxiliary events.

- The phone shall support diagnostic logging for the following modules:

- Audio

- Call Control

- Command Module

- Device Control

- SIP Module

- Timer

- The phone shall support storage of logs in internal memory. Once the storage limit is reached, the phone will automatically overwrite with new logging data.

- The phone shall be user configurable to transmit logging data to a SYSLOG server.

- Self-Diagnostic Testing

- The phone shall support self-diagnostic testing and reporting of the following hardware:

      - Button/Switch integrity

      - Speaker and Microphone audibility test

      - Microphone and Line-level output audibility test

- The phone shall be user configurable to report self-diagnostic test results by:

- Placing a phone call to a user specified number.

- Emailing a report to a user specified email recipient.

- Protocol Support

- The phone shall incorporate support for at least IP, HTTP, TCP, UDP, ICMP, RTP, SDP, SIP, RTCP, FTP, SSH, DHCP, ARP, DNS, and NTP.

- Installation and Maintenance

- The phone shall allow updates of the software (firmware) over the network, using FTP or HTTP.

- Customer-specific settings, including statically assigned IP address, the local time and date, event functionality and audio configuration, shall be stored in non-volatile memory and shall not be lost during power cuts or soft reset.

2.05   INTERFACES

- Audio

  - The phone shall be equipped with one line-level output, accessible from a removable terminal block.

  - The output shall have an impedance of 10K Ω

- Inputs/Outputs

  - The phone shall be equipped with three auxiliary inputs, accessible from a removable terminal block.

    - The inputs are rated up to 10mA @ 8VDC each.

    - The inputs are opto-isolated, with isolated grounds.

  - The phone shall be equipped with three auxiliary outputs, accessible from a removable terminal block.

    - The outputs are rated up to 120mA @ 120VAC/DC each.

    - The outputs are opto-isolated, with isolated grounds.

- Network Interfaces

  - The phone shall be equipped with two 100baseTX Fast Ethernet ports, and shall support auto sensing of network speed.

  - The second Ethernet port is designated a LAN port, and serves as a pass-through switch-port for third-party devices.

2.07   POWER REQUIREMENTS

- The phone shall be powered by one of the following power sources:

  - Power over Ethernet according to IEEE802.3af – Class 3.

  - 12VDC, dedicated line-regulated power supply – Nominal: 500mA; Maximum: 800mA

  - 24VDC, dedicated line-regulated power supply – Nominal: 300mA; Maximum: 500mA

  - 24VAC, dedicated line-regulated power supply – Nominal: 300mA; Maximum: 500mA

2.08   ENVIRONMENTAL

- The phone shall:

  - Operate in a temperature range of -40°F (-40°C) to + 131°F (+55°C).

  - Operate in a humidity range up to 95% RH (non-condensing).

2.09   MANUFACTURED UNITS

- The phone shall be a Talkaphone VOIP-600 Series IP Call Station.

PART 3 EXECUTION

3.01      INSTALLATION

- The installer shall carefully follow instructions in documentation provided by the manufacturer to ensure all steps have been taken to provide a reliable, easy-to-operate system.

- All equipment shall be tested and configured in accordance with instructions provided by the manufacturer prior to installation.

- All firmware found in products shall be the latest and most up-to-date provided by the manufacturer.

- All equipment requiring users to log on using a password shall be configured with user/site-specific password(s). No system/product default passwords shall be allowed.

END OF SECTION